Task 123 - Underwater – Install and Remove a Completion Plug on a Pipeline System

1.0 Task Description

This task involves the installation of a completion plug to tightly seal the fitting and allow installation and removal of the valve used in conjunction with a tapping machine or plugging machine. This task is similar to Task 40.9 (Install and Remove Completion Plug Larger Than 2 in. on a Pipeline System) and Task 40.11 (Install and Remove Completion Plug 2 in. and Under on a Pipeline System) but contains steps or equipment that are unique to an underwater environment.

This task begins with installation of the tapping machine on the tapping valve. This task ends with the installation of a cap, blind flange, piping, instrumentation, or other component onto the fitting.

2.0 Knowledge Component

A completion plug is used to seal the fitting to allow removal of the valve after completion of a hot tap. The completion plug prevents the release of product while a blind flange, piping, valve, or other component is being attached to the fitting. The completion plug can be subsequently removed from the fitting to install a plugging machine.

An individual performing this task must have knowledge of:

- The notification(s) that must be completed prior to and/or after the task is completed, according to relevant Operator procedures.

Terms applicable to this task.

Containment equipment

Equipment such as containment domes, diaphragms, pumps, hoses, and receiving tanks (MPT Tanks) to capture hydrocarbons.

Completion plug

A plug designed to seal the opening created by a hot tap and allow installation and removal of the valve.

Fitting

A component welded or clamped to the pipeline upon which a valve is installed to allow tapping and plugging.

Plugging machine

A machine installed onto the appropriate valve for the purpose of cutting a hole into a pipeline or breakout tank and installing and removing completion plugs

Tapping machine/drilling machine

A machine installed onto the appropriate tapping valve for the purpose of boring a hole into a pipeline or breakout tank

Tapping valve

The component installed on the fitting to control product flow while inserting the boring bar and operating the cutter on the pipeline or breakout tank and during removal of the tapping machine.

Abnormal operating conditions (AOC) associated with the performance of this task include:

| AOC Recognition | AOC Reaction |
| --- | --- |
| Damage (e.g. mechanical damage or corrosion) to pipeline facilities or components. | Make appropriate notifications and follow applicable operator procedures. |
| Malfunction of or damage to tapping machine, tapping valve, or other related equipment that has the potential for loss of product. | Stop operation and secure the equipment if safe to do so. Inspect the equipment and readjust or reset as necessary. |
| Unexpected release of pressure or product from pipeline or completion plug. | Stop operation and secure the equipment if safe to do so. Immediately notify the operator or responsible person and initiate applicable emergency procedures. Remove completion plug or leaking component, inspect or replace components, and reinstall the plug in the fitting. |

3.0 Skill Component

To demonstrate proficiency of this task, an individual must perform the following steps:

| Step | Action | Explanation |
| --- | --- | --- |
| 1 | Assemble plug and plug holder to the boring bar. | Confirms proper assembly of compatible components and the plug correctly fits the void and remains in place once installed, as well as correct retrieval and removal of the plug. |
| 2 | Inspect and assemble tapping machine and plug holder components. | Verifies components are in good condition. |
| 3 | Take necessary measurements prior to installing the tapping machine on the valve. | Confirms proper seating location. |
| 4 | Install tapping machine onto the valve with the plug holder fully retracted. | Prevents damage to tapping machine. |
| 5 | Prior to opening the valve, equalize the pressure on each side of the valve if possible. | Equalized pressure facilitates operation of tapping machine and/or valve. |
| 6 | Slowly open the valve fully on the fitting. | The valve shall be fully opened to allow insertion of the completion plug. |
| 7 | Lower the completion plug into the fitting with the boring bar. Verify proper alignment and initial depth measurements according to appropriate underwater procedures. | Diver verifies that the plug is mechanically positioned correctly with set screw resistance and turn count. |
| 8 | Confirm plug is properly set. | Confirms proper containment of product in the pipeline. |
| 9 | Safely relieve pressure using the tapping machine annulus needle valve. | Confirms proper depressurization and containment of product within tapping machine assembly. |
| 10 | Confirm that the plug is properly sealed. | Allows proper removal of the tapping machine, valve and installation of the cap, blind flange, etc. |
| 11 | Set up containment equipment and remove the tapping machine from the valve. |  |
| 12 | Remove the valve |  |
| 13 | Install the gasket, blind flange, piping, instrumentation, or other component onto the fitting or valve. |  |