Task 9.6.4—Install Electrical Insulating Device—Lightning Protection and Electrical Grounding

1.0	Task Description

This task consists of installing electrical insulating devices for lightning protection and electrical grounding.

The task begins when the required installation location of the isolation device is identified. This task ends when isolation device has been installed, tested, and documented according to the operator’s procedure.

The performance of this covered task may require the performance of other covered tasks such as:

Measure Structure-to-soil Potentials (reference Task 1.1);

Test to Detect Interference (reference Task 1.3);

Inspect and Test Electrical Isolation (reference Task 1.5).

2.0	Knowledge Component

The purpose of this task is to isolate pipeline segments and equipment from lightning protection or electrical ground fault system to ensure proper functioning of cathodic protection (CP) systems.

An individual performing this task shall have knowledge of:

CP systems;

electrical isolation;

grounding systems;

various electrical isolation devices, such as a polarization cell replacement (PCR) or a solid-state decoupling (SSD) device.

Terms associated with this task:

This section intentionally left blank.

Abnormal operating conditions (AOCs) associated with the performance of this task include the following:

| AOC Recognition | AOC Reaction |
| --- | --- |
| Unexpected hazardous product encountered. | Stop task activities, eliminate ignition source(s), and notify appropriate personnel. |
| Discovery of damage (e.g. mechanical damage or corrosion) on pipeline facilities or components. | Make appropriate notifications and follow the operator’s procedures. Complete other actions, including documentation, as required. |
| Abnormal or erratic readings on test equipment. | Make appropriate notifications and follow the operator’s procedures. Complete other actions, including documentation, as required. |
| The removal of power results in the unintentional activation of a safety/control device. | Take appropriate action to mitigate the situation and to return the pipeline to normal condition. Notify the control center or local operations. |

3.0	Skill Component

To demonstrate proficiency of this task, an individual shall perform the following steps:

| Step | Action | Explanation |
| --- | --- | --- |
| 1 | Verify the location where the isolation device is needed. | This step verifies that the installation will be appropriately mounted, enclosed, and compatible with the location of the installation. |
| 2 | Install all insulating devices in accordance with the manufacturer’s specifications. | For lightning and ground fault protection, the equipment typically consists of either a PCR or an SSD device that is bonded sufficiently and oppositely on both sides of the insulating flange. For electrical grounding, provision for electrical isolation through an approved electrical device (PCR or SSD) that is rated for the service shall be made at main line valves, densitometers, flow-meters, pressure transmitters, and other sites where such structures will be in bare metal contact to the soil. |
| 3 | Verify isolation with the appropriate isolation tester. | NOTE The completion of this step may be completed by another individual qualified in Task 1.5—Inspect and Test Electrical Isolation. For electrical grounding, conduct testing on all utility (electrical, telephone, etc.) supply or feeder cables to identify direct current flow to the foreign structures. This may require the completion of Task 1.1—Measure Structure-to-soil Potentials, and Task 1.3—Test to Detect Interference. |
| 4 | Record all required documentation per the operator’s procedures. | Proper documentation is critical to future analysis and identification of problem areas. |